## Slide 1
Reaching Conclusions

## Slide 2: Today's Session
Open forum – questions – ask them
Review NAWT Conclusions
Offer different scenarios
Discuss how we reach conclusions
Your experiences

## Slide 3: Who Are You?
Please introduce yourself
Where are you from?
Are you NAWT Certified?
What services you provide

## Slide 4: Conclusions
Turn to Chapter Six - page 45 in the NAWT OWTS Inspection Standards Manual
Notes: We are going to bring all the information we have been covering together now to arrive at the final Conclusion
We will be going over how to use the manual to reach the conclusion
We will be using scenarios and examples and discussing how to arrive at the appropriate conclusion

## Slide 5
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure age - 3 yrs. | Septic Concrete 1,000 Gallons Last pumped - Unknown Condition - OK | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | No surface discharge; no lush vegetation; runback observed at time of tank pumping. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – TREATMENT, HOLIDNG, DOSING, LIFT AND SIPHON TANKS – 2. THE BACKFLOW/RUNBACK OF LIQUID FROM THE STA AFTER PUMPING THE TREATMENT TANK

## Slide 6
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
4 Bedrooms Occupied Structure age - 15 yrs. | Septic Concrete 1,500 Gallons Last pumped – Every 2 yrs. | OK | Gravity | Trenches 12 inches dry aggregate in all trenches
COMMENTS: | All past pump-outs through 4-inch observation port. Main tank access is 4 feet below grade; tank not dug open. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 54 – TREATMENT TANK – 2. CANNOT ACCESS THE MAIN ACCESS PORT(S) OF THE TREATMENT TANK

## Slide 7
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied 4 Occupants Structure age - 10 yrs. | Septic Plastic 1,000 Gallons Condition - OK | OK | Gravity | Trenches 12 inches dry aggregate in all trenches
COMMENTS: |  |  |  | 
Notes: CONCLUSION: ACCEPTABLE

## Slide 8
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Vacant for 3 months Structure age - 10 yrs. | Septic Concrete 1,000 Gallons Last pumped – Every 2 yrs. Condition - OK | OK | Gravity | Bed 0 inches dry aggregate throughout bed
Notes: CONCLUSION: UNACCEPTABLE
PAGE 52 – SOIL TREATMENT AREA – 2. STA IS SATURATED TO THE FULL DEPTH OF THE AGGREGATE

## Slide 9
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
2 Bedrooms Occupied 1 Occupant Structure age - 5 yrs. | Septic Concrete 1,000 Gallons Last pumped – Unknown Condition - OK | OK | Gravity | Trenches 12 inches dry aggregate in all trenches
COMMENTS: | No maintenance/service history. Soil fracturing 2 weeks before inspection. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 55 – SOIL TREATMENT – 4. SOIL FRACTURING ACTIVITY WITHIN THE LAST 30 DAYS (CONDUCT AN HLT*)

## Slide 10
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied 4 Occupants Structure age - 10 yrs. | Septic Concrete 1,000 Gallons Condition - OK | OK | Gravity Pump | Bed 2 inches dry aggregate throughout bed
COMMENTS: | Lift pump to conventional (gravity) bed; 2 occupants moving in; no lush vegetation. |  |  | 
Notes: CONCLUSTION: NEEDS MORE INVESTIGATION
PAGE 55 – DISTRIBUTION SYSTEMS – 3. IN A GRAVITY FED DISTRIBUTION SYSTEM, IF THERE IS LESS THAN 5” OF DRY AGGREGATE (CONDUCT AN HLT*)

## Slide 11
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure age - 12 yrs. | Septic Concrete Last pumped - every 2 yrs. for past 10 yrs. Condition - OK | 1 inch Below outlet | Gravity | Trenches 12 inches dry aggregate in all trenches
COMMENTS: | No history of problems. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – TREATMENT, HOLDING, DOSING, LIFT AND SIPHON TANKS – 1. AN UNACCEPTABLE TREATMENT TANK LIQUID LEVEL OCCURS WHEN THE LIQUID LEVEL IS ABOVE THE INLTER INVERT AND ABOVE OR BELOW THE HEIGHT OF THE OUTLET INVERT

## Slide 12
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
5 Bedrooms 6 Toilets 1 Hot tub Occupied Structure age - 4 yrs. | Septic Concrete 1,500 Gallons | OK | Gravity | ESM Bed - gravity 10 inches dry aggregate throughout bed
COMMENTS: | Outlet baffle ok; inlet baffle missing – local code requires inlet baffle/tee on all tanks. |  |  | 
Notes: CONCLUSTION: UNACCEPTABLE
PAGE 51 – TREATMENT, HOLDING, DOSING, LIFT AND SIPHON TANK – 6. MISSING COMPONENT

## Slide 13
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
2 Bedrooms 3 Occupants Occupied Structure age - 7 yrs. | Septic Concrete 1,000 Gallons Condition - OK | OK | Siphon | ESM Bed - pressure 10 inches dry aggregate throughout bed
COMMENTS: |  |  |  | 
Notes: CONCLUSION: ACCEPTABLE

## Slide 14
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
4 Bedrooms 9 Occupants Occupied Structure age - 6 yrs. | Septic Plastic 1,500 Gallons Condition - OK | OK | Pump | Bed 12 inches dry aggregate throughout bed
COMMENTS: | Alarm system not working; no pumping history. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – GENERAL – 3. NON-FUNCTIONING (NOT WORKING AS INTENDED) ELECTRICAL COMPONENTS (AEROBIC DEVISE, PUMP, CONTROLS, OR ALARMS)

## Slide 15
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
4 Bedrooms 2 Occupants Occupied Structure age - 6 yrs. | Septic Concrete 1,500 Gallons Condition - OK | OK | Pump Alarm | ESM Bed - pressure 10 inches dry aggregate throughout bed
COMMENTS: | Electrical tape used to wrap pump and alarm wire’s splices. |  |  | 
Notes: CONCLLUSION: ACCEPTABLE WITH CONCERNS
PAGE 49 – TREATMENT, HOLDING, DOSING, LIFT, AND SIPHON TANKS – 9. QUESTIONABLE WIRING AND CONNECTIONS THAT ARE STILL FUNCTIONAL

## Slide 16
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
4 Bedrooms 2 Occupants Occupied Structure age - 11 yrs. | Septic Concrete 1,500 Gallons Last pumped - Never Condition - OK | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | Family of six moving in; tank never pumped prior to inspection. |  |  | 
Notes: CONCLUSTION: ACCEPTABLE WITH CONCERNS
PAGE 48 – GENERAL – 4. SYSTEM OVER 10 YEARS OLD WITH NO MAINTENANCE RECORDS

## Slide 17
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Hot tub Vacant for 6 months | Septic Concrete 1,000 Gallons Last pumped - Unknown Condition - OK | OK | Gravity | Trenches 12 inches dry aggregate in all trenches
COMMENTS: |  |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 53 GENERAL – 1. STRUCTURE VACANT MORE THAN 7 DAYS (CONDUCT A HYDRAULIC LOAD TEST

## Slide 18
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
5 Occupants Occupied | Septic Concrete 1,200 Gallons Last pumped – 9 months Condition - OK | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | When pumped 9 months ago liquid ran back from Soil Treatment area. Leaky toilet found; owner reports he fixed it. |  |  | 
Notes: CONCLUSTION: ACCEPTABLE

## Slide 19
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure age - 10 yrs. | Aerobic 1,000 Gallons Concrete | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | Aerator tested; found to be not working. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – GENERAL – 3. NON-FUNCTIONING (NOT WORKING AS INTENDED) ELECTRICAL COMPONENTS (AEROBIC DEVISE, PUMP, CONTROLS, OR ALARMS)

## Slide 20
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms 1 Hot tub Occupied Structure age - 35 yrs. | Septic Plastic 1,000 Gallons Last pumped – Unknown Condition - OK | OK | Gravity | See Comments
COMMENTS: | Soil Treatment area not located with hand tools. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 55 – SOIL TREATMENT AREA – 1. THE STA CAN’T BE LOCATED WITH HAND TOOLS – THE STA MUST BE LOCATED TO BE INVESTIGATED

## Slide 21
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Vacant Structure age - 35 yrs. | Septic Plastic 1,200 Gallons Condition - OK | OK | Gravity | See Comments
COMMENTS: | Aggregate filled pit (5 feet x 5 feet x 4 feet) interior dry to full depth. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 53 – GENERAL – 1. STRUCTURE VACANT FOR MORE THAN 7 DAYS (CONDUCT AN HLT)

## Slide 22
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Vacant for 5 weeks Structure age - 35 yrs. | Concrete 1,000 Gallons Condition - OK | OK | Gravity | Bed
COMMENTS: | Hydraulic load test results - Day 1 added 400 gal; rose to 1 inch below top of aggregate. Day 2 added 300 gal; rose to 1 inch below top of aggregate. |  |  | 
Notes: CONCLUSTION: UACCEPTABLE
PAGE 53 – SOIL TREATMENT AREA – 10. IN THE COURSE OF AN HLT, IF AN STA FAILS TO ACCEPT THE CACLUATED DAILY FLOW AND THE LIQUED LEVEL REMAINS AT OR ABOVE THE TOP OF THE AGGREGATE OR THE LOWEST POINT OF THE INLET PIPE IN A CESSPOOL OR SEEPAGE PIT.

## Slide 23
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms 2 Occupants Structure age - 25 yrs. | Septic Concrete 1,000 Gallons Condition - OK | OK | Gravity | See Comments
COMMENTS: | TWO Soil Treatment areas connected w/ bull run valve. Valve currently sends all flow to Soil Treatment area #2. #1 Conventional bed, dry aggregate throughout. #2 Aggregate filled pit, liquid above top of aggregate. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 56 – SOIL TREATMENT AREA – 10. TWO SOIL STAs CONNECTED WITH A DIVERTER VALVE. IF ONE IS UNACCEPTABLE AND THE SECOND SYSTEM SHALL BE TESTED TO VERIFY IT IS ACCEPTABLE

## Slide 24
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied | Aerobic Concrete 1,000 Gallons Condition - OK | OK | Gravity Pump | Trenches 3 inches dry aggregate in all trenches
COMMENTS: | Lift Pump |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 55 – SOIL TREATMENT AREA – 8. IN A GRAVELLESS CHAMBER SYSTEM, IF THERE ARE LESS THAN FIVE INCHES OF CLEAR SPACE BETWEEN THE TOP OF THE STANDING LIQUIED AND THE UNDERSIDE OF THE CHAMBER (CONDUCT AN HLT)

## Slide 25
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied | Septic Concrete 1,000 Gallons Condition - OK | OK | Gravity | Bed 4 inches dry aggregate throughout bed
COMMENTS: | Hydraulic load test results - Day 1 - 300 gal. brought liquid level to top of aggregate. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 56 – SOIL TREATMENT AREA – 12. HLT NOT FOLLOWED THROUGH TO THE SECOND DAY

## Slide 26
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms 5 toilets 1 Hot tub Vacant for 3 months | Concrete 1,000 Gallons Condition - OK | OK | Gravity | See Comments
COMMENTS: | Soil Treatment area is a seepage pit - no measurable liquid present. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 56 – SOIL TREATMENT AREA – 11. DRY AGGREGATE RULES DICTATES AN HLT

## Slide 27
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
5 Bedrooms Occupied | 5,000 Gallons Last pumped - Unknown | See Comments | Gravity | See Comments
COMMENTS: | Cesspool with less than 1 day’s capacity between operating liquid level and bottom of inlet pipe. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 55 – SOIL TREATMENT AREA – 3. A CESSPOOL OR SEEPAGE PIT WITH LESS THAN 24-HOURS VOLUME CAPACITY BETWEEN OPERTING LEVEL AND THE INLET INVERT (CONDUCT AN HLT)

## Slide 28
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
5 Bedrooms 6 Occupants Occupied Structure age – 8 months | 2 septic tanks Concrete 1,000 Gallons each | See Comments | Gravity | Trenches 10 inches dry aggregate in all trenches
COMMENTS: | Two 1,000-gallon tanks in series. Level in tank #1 is OK. Level in tank #2 is 1 inch below outlet. Well is 40 feet from Soil Treatment area. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – TREATMENT, HOLDING, DOSING, LIFT, AND SIPHON TANKS – 1. AN UNACCEPTABLE TREATMENT TANK LIQUID LEVEL OCCURS WHEN THE LIQUID LEVEL IS ABOVE THE INLET INVERT AND ABOVE OR BELOW THE HEIGHT OF THE OUTLET INVERT
IN ADDITION – THERE IS A CONCERN AS TO HOW CLOSE THE WELL IS TO THE STA – MOST AREA REQUIRE AT LEAST 100’

## Slide 29
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Structure age – 2 yrs. | 2 septic tanks Concrete 1,000 Gallons Last pumped – Unknown See Comments | OK | Pump OK Floats OK Alarm | ESM bed - pressure 10 inches dry aggregate throughout bed
COMMENTS: | Treatment tank #1 - Condition OK. Treatment tank #2 - Solids retainer/Effluent screen found in bottom of tank. |  |  | 
Notes: CONLUSION: UNACCEPTABLE
PAGE 52 – SCREEN – TYPE EFFLUENT FILTERS – 1. FILTER IS DAMAGE OR FILTER HAS BEEN REMOVED FROM THE TANK WHERE IT ONCE EXISTED

## Slide 30
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure age – 24 yrs. | Septic Plastic 1,000 Gallons Condition - OK | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | Sump pump discharges to building sewer; 18-inch diameter tree growing in Soil Treatment area. No maintenance history. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – GENERAL – 1. DISCHARGES FROM ANY OF THE FOLLOWING TO ANY PART OF THE ONSITE OWTS: SUMP PUMP, FOOTER DRAIN, ROOF DRAINS AND/OR DOWNSPOUTS

## Slide 31
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
5 Bedrooms Hot tub Structure age – 2 yrs. | Septic Concrete 1,000 Gallons Condition - OK | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | Inlet observation port not present. |  |  | 
Notes: CONCLUSION: ACCEPTABLE WITH CONCERNS
PAGE 48 – TREATMENT, HOLDING, DOSING, LIFT, AND SIPHON TANKS – 3. NO ACCESS PORT(S) OR OBSERVATION PORT(S) TO GRADE OVER TREATMENT TANK INLET

## Slide 32
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
6 Bedrooms 4 toilets 2 Hot tubs Occupied Structure age – 2 yrs. | 2 Septic Concrete 1,000 Gallons each Condition – OK in both | OK | Gravity | Trenches 12 inches dry aggregate in all trenches
COMMENTS: | Continuous flow through building sewer to treatment tank. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 50 – GENERAL – 4. A CONSTANT FLOW OF LIQUID FROM THE STRUCTURE THROUGH THE BUILDING SEWER

## Slide 33
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure age – 25 yrs. | Septic Concrete 1,200 Gallons Last pumped – 60 months Condition – OK | OK | Gravity D-Box | Soil Treatment No uniform distribution
COMMENTS: | Four trenches dry; one trench - no dry aggregate; concrete D-box crumbling. |  |  | 
Notes: CONCLUSION: UNACCEPTABLE
PAGE 52 – DISTRIBUTION SYSTEMS – 1. CLOGGED OR BROKEN EFFLUENT DELIVERY LINES OR OTHER PIPES IMPEDING PROPER EFFLUENT DELIVERY / ALSO: 56 – NMI STA – 9 UNEQUAL AMOUNT OF DRY AGGREGATE IN STA – IF THERE IS NOT DRY AGGREGATE IN ANY PORTION OF THE STA IT IS UNACCEPTABLE

## Slide 34
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure age – 35+ yrs. | Concrete 1,000 Gallons Last pumped – 6 yrs. Condition – OK | OK | Gravity | Trench 7 inches dry aggregate in each trench
COMMENTS: | Laundry gray water bypasses treatment tank and goes directly to Soil Treatment area. |  |  | 
Notes: CONCLUSION: ACCEPTABLE WITH CONCERNS
PAGE 47 – GENERAL – 2. SYSTEMS INCLUDING GRAY WATER DISCHAGES OF THE FOLLOWING NATURE, WHEN FOUND IN CONJUNCTION WITH AN OTHERWISE ACCEPTABLE SYSTEM SHAL ALWAYS BE DESCRIBED AS AWC: GRAY WATER DISCHAGES THAT BYPASS THE TREATMENT TANK AND ARE DIRECTED TO THE PRIMARY STA EITHER DIRECTLY OR THOUGH AN EFFLUENT DISTRIBUTION SYSTEM. SOILDS IN THE GRAY WATER MAY DAMAGE THE STA. ALL WASTEWATER FROM THE BUILDING SHOULD BE DIRECTE TO THE TREATMENT TANK

## Slide 35
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
2 Bedrooms Vacant for 6 months Structure age – 25 yrs. | See Comments | See Comments | Gravity | Bed 8 inches dry aggregate throughout bed
COMMENTS: | Treatment tank under concrete patio; only access is a 4-inch observation port; owner will allow “no more testing; no holes in patio to access main tank manhole.” |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 54 – TREATMENT TANK – 2. CANNOT ACCESS THE MAIN ACCESS PORT(S) OF THE TREATMENT TANK.

## Slide 36
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms Occupied Structure built 1962 | Septic Concrete 1,000 gallons | OK | Gravity | Bed 12 inches dry aggregate throughout bed
COMMENTS: | Tree over main tank access; observation port used as pump-out access. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 54 – TREATMENT TANK – 2. CANNOT ACCESS THE MAIN ACCESS PORT(S) OF THE TREATMENT TANK.

## Slide 37
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
4 Bedrooms Hot tub Structure age – 40+ yrs. Occupied 6 months each yr. Summer home, currently vacant 2 months | See Comments | OK | Gravity | See Comments
COMMENTS: | Cesspool with two compartments. Only one compartment accessible, combined remaining unused capacity unknown. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 55 – SOIL TREATMENT AREA – 2. CANNOT PROPERLY ACCESS THE CESSPOOL OR SEEPAGE PIT IN ORDER TO INSPECT IT.

## Slide 38
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
5 Bedrooms Occupied Structure age – 20+ yrs. | Aerobic Concrete 1,500 gallons Condition - OK | OK | Gravity | Bed 1 inch's dry aggregate throughout bed
COMMENTS: | 6 feet x 12 feet x 8 feet aggregate filled pit next to bed with 69 inches dry aggregate. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 32 – DRY AGGREGATE RULE – NO SAND – GRAVITY – LESS THAN OR EQUAL 5” BUT GREATER THAN 0” – HYDRAULIC LOAD TEST

## Slide 39
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
1 Occupant Occupied Structure age – 35+ yrs. | Septic Concrete Last pumped – 1 yr. Condition - OK | OK | Gravity | 4 trenches 12 inches dry aggregate in each trench
COMMENTS: | Sludge throughout aggregate and sludge stains in soil 6-inches above aggregate. |  |  | 
Notes: CONCLUSION: NEEDS MORE INVESTIGATION
PAGE 53 – GENERAL – 2. SIGNS OR REPORTS OF PREVIOUS UNACCEPTABLE PERFORMANCE – BULLET 2 STAINS IN SOILS ADJACENT TO TANKS, ON SURFACE, ETC.

## Slide 40
Occupancy | Tank Structure | Liquid Level | Effluent Delivery | Soil Treatment Area
3 Bedrooms 3 Occupants Occupied Structure age – 10 yrs. | Septic Metal 1,000 gallons Condition - OK | OK | Gravity | 4 trenches 12 inches dry aggregate in each trench
COMMENTS: |  |  |  | 
Notes: CONCLUSION: ACCEPTABLE

## Slide 41: Your Experiences

## Slide 42: Conclusion
We’ve reached our conclusion
Any question?